## 1.Approach
SECI Assured Peak Supply (APS) under CfD — Solar + BESS Bid Model
100 MW contract ¦ 3-hour evening peak ¦ Solar PV + Battery hybrid ¦ Target Project IRR 12%
OBJECTIVE
Size a Solar + BESS portfolio to firmly deliver 100 MW for 3 hours in the evening peak, find the minimum
CfD strike price that earns a 12% project IRR, value the merchant surplus on 3-yr IEX DAM prices, and
test the sensitivity of equity returns and pool cost to a +/-10% move in market prices.
HOW THE MODEL WORKS (5 steps)
Step 1 - Size BESS | Fixed by the contract: 100 MW power, 4-hour product (400 MWh nameplate). After 87% round-trip
efficiency it comfortably delivers the 300 MWh needed in the 3h peak, with headroom for degradation.
Step 2 - Size Solar | Set by the reliability of charging the battery every day, NOT by merchant economics. At IEX midday
prices (~Rs 3/kWh) extra solar is roughly value-neutral, so we build the minimum overbuild that assures
charging across seasons: 1.5x = 150 MW. The strike penalty vs a 1.0x build is only ~Rs 0.1/kWh (see 3.Sizing).
Step 3 - Energy balance | Solar first charges the battery (300/0.87 = 345 MWh/day); the surplus is sold merchant in the day.
Step 4 - Solve strike | Build a 25-yr post-tax unlevered cash flow. Peak energy earns the strike; surplus earns the DAM day price.
Goal-seek the strike so Project IRR = 12% (see 4.Cashflow). Result ~ Rs 10.8/kWh.
Step 5 - Sensitivity | Layer 70:30 debt for Equity IRR, then flex market price +/-10% to see impact on EIRR and pool cost (6.Sensitivity).
CfD SETTLEMENT LOGIC
Two-way CfD on the 300 MWh/day peak block. If DAM peak price < strike, SECI tops the developer up to strike.
If DAM peak price > strike, the gain above strike is shared 50:50. Merchant day-surplus is 100% the developer's.
KEY RESULTS
Recommended sizing | Solar 150 MW + BESS 100 MW / 4h (400 MWh) ¦ Total capex Rs 950 Cr
Required strike price | ~ Rs 10.8 / kWh (12% post-tax project IRR, straight-line depreciation)
Equity IRR (70:30 debt) | ~ 17.4%
Sensitivity (+/-10% price) | EIRR moves to 18.4% / 16.3% ; SECI pool top-up moves to 46 / 59 Cr per year
READ ME | Blue cells = inputs you can change. Black = formulas. Green = links to other tabs. Yellow = key levers.
All assumptions and sources are on tab 2.Assumptions. Change an input and re-open to recalc.

## 2.Assumptions
ASSUMPTIONS (blue = input)
Parameter | Value | Unit | Rationale / Source
CONTRACT & TECHNICAL
Contract capacity | 100 | MW | SECI APS tender requirement (given in brief)
Peak supply duration | 3 | hours | Tender: 3h assured peak window
Peak window | 18:00-21:00 |  | Assumption: evening demand peak; solar absent so needs BESS; highest DAM prices. Ref: SECI FDRE/peak RfS peak-hour definition
Peak energy delivered/day | 300 | MWh | capacity x hours = 300 MWh
Days per year | 365 | days | Assumed 100% peak availability (assured-supply obligation)
SOLAR
Solar capacity (chosen) | 150 | MW | Recommended 1.5x overbuild for reliable daily charging (see 3.Sizing). INPUT you can flex.
Solar CUF | 0.21 | ratio | Typical Indian utility solar 19-22%. Assumption 21%. Ref: CERC/MNRE benchmark, historical plant data
Solar degradation | 0.005 | /yr | 0.5%/yr module degradation - industry standard (mfr warranties)
Solar capex | 4 | Rs Cr/MW | Given in brief (key input 1)
BESS
BESS power (chosen) | 100 | MW | contract power; must deliver 100 MW in peak
BESS duration (product) | 4 | hours | Capex quoted for 4h product; 4h gives headroom over 3h need
BESS round-trip efficiency | 0.87 | ratio | Li-ion RTE ~85-90%. Assumption 87%. Ref: NREL/BNEF storage data
BESS capex (4h) | 3.5 | Rs Cr/MW | Given in brief (key input 2). Includes augmentation reserve via O&M
Energy to charge/day | 344.8276 | MWh | 300 / RTE = 345 MWh (AC into battery)
MARKET PRICES (IEX DAM, 3-yr indicative)
DAM peak-hour price | 6 | Rs/kWh | 3-yr avg evening-peak DAM. Ref: IEX Day-Ahead Market MCP FY22-FY24 (iexindia.com). INDICATIVE - replace with downloaded 18-21h data
DAM solar-hour price | 3 | Rs/kWh | 3-yr avg midday DAM (solar depresses prices). Ref: IEX DAM MCP FY22-FY24. INDICATIVE - replace with 10-16h data
Merchant price escalation | 0.03 | /yr | Assumption 3%/yr nominal, below general inflation (RE glut caps day prices)
OPERATING & FINANCIAL
Solar O&M (% capex, yr1) | 0.01 | /yr | 1.0% of solar capex. Ref: CERC RE tariff O&M norms
BESS O&M (% capex, yr1) | 0.025 | /yr | 2.5% - higher, includes battery augmentation reserve for capacity fade
O&M escalation | 0.05 | /yr | 5.0%/yr - CERC standard O&M escalation
Project life | 25 | years | Standard solar PPA/asset life; battery augmented to match
Target project IRR | 0.12 | ratio | Given in brief (post-tax, unlevered)
Corporate tax rate | 0.25 | ratio | ~25% (concessional 22% + surcharge/cess). Simplified. Ref: Income Tax Act sec 115BAA
Depreciation method | Straight-line |  | SL over 25y for tax (simple/conservative). Note: accelerated dep would lower strike ~Rs 0.6
FINANCING (for Equity IRR)
Debt : Equity | 0.7 | debt frac | 70:30 typical RE project finance
Interest rate | 0.09 | /yr | 9% INR term debt (indicative)
Debt tenor | 15 | years | 15-yr amortisation, equal principal
Gain-share above strike | 0.5 | dev share | Developer keeps 50% of upside above strike (assumption; confirm vs tender RfS)

## 3.Sizing
SIZING LOGIC & ENERGY BALANCE
A. Energy balance (annual, year 1)
Solar generation, yr1 | 275940 | MWh | MW x 8760 x CUF
Energy needed to charge BESS | 125862.069 | MWh | ~345 MWh/day x 365
Merchant surplus (day sales) | 150077.931 | MWh | solar gen - charging
Peak energy delivered (CfD) | 109500 | MWh | 300 x 365
B. CAPEX
Solar capex | 600 | Rs Cr
BESS capex | 350 | Rs Cr
Total capex | 950 | Rs Cr
C. Why 150 MW solar? (strike vs overbuild - illustrative, from model)
Solar MW | Overbuild | Merchant GWh | Strike Rs/kWh | Assured supply?
100 | 1.0x | 58 | 10.69 | Tight - fails on cloudy days
120 | 1.2x | 95 | 10.74 | Marginal
150 | 1.5x | 150 | 10.81 | ROBUST <-- chosen
180 | 1.8x | 205 | 10.88 | Robust but excess capex
220 | 2.2x | 279 | 10.98 | Over-exposed to merchant
Takeaway: strike is nearly flat vs overbuild (merchant is ~value-neutral at Rs 3/kWh),
so solar size is driven by charging RELIABILITY. 1.5x assures the peak obligation at only ~Rs 0.1/kWh premium.

## 4.Cashflow
UNLEVERED CASH FLOW -> SOLVE STRIKE FOR 12% PROJECT IRR
Strike (Rs/kWh): | 10.81 | <- goal-seek: change until Project IRR (B3) = 12.0%
Project IRR (target 12.0%) | 12%
Project NPV @ 12% (Rs Cr) | -0.04374
Line item (Rs Cr unless noted) | Unit | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Solar generation | MWh | 0 | 275940 | 274560.3 | 273187.4985 | 271821.561 | 270462.4532 | 269110.1409 | 267764.5902 | 266425.7673 | 265093.6384 | 263768.1703 | 262449.3294 | 261137.0828 | 259831.3973 | 258532.2404 | 257239.5792 | 255953.3813 | 254673.6143 | 253400.2463 | 252133.245 | 250872.5788 | 249618.2159 | 248370.1248 | 247128.2742 | 245892.6329 | 244663.1697
Merchant surplus | MWh | 0 | 150077.931 | 148698.231 | 147325.4295 | 145959.492 | 144600.3842 | 143248.072 | 141902.5213 | 140563.6983 | 139231.5695 | 137906.1013 | 136587.2604 | 135275.0138 | 133969.3284 | 132670.1714 | 131377.5102 | 130091.3123 | 128811.5454 | 127538.1773 | 126271.1761 | 125010.5099 | 123756.147 | 122508.0559 | 121266.2053 | 120030.5639 | 118801.1007
Peak delivered | MWh | 0 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500 | 109500
Merchant price | Rs/kWh |  | 3 | 3.09 | 3.1827 | 3.2782 | 3.3765 | 3.4778 | 3.5822 | 3.6896 | 3.8003 | 3.9143 | 4.0317 | 4.1527 | 4.2773 | 4.4056 | 4.5378 | 4.6739 | 4.8141 | 4.9585 | 5.1073 | 5.2605 | 5.4183 | 5.5809 | 5.7483 | 5.9208 | 6.0984
Merchant revenue | Cr | 0 | 45.0234 | 45.9478 | 46.8893 | 47.8482 | 48.8247 | 49.8191 | 50.8317 | 51.8627 | 52.9123 | 53.9809 | 55.0686 | 56.1757 | 57.3025 | 58.4492 | 59.6161 | 60.8034 | 62.0114 | 63.2404 | 64.4905 | 65.762 | 67.0552 | 68.3703 | 69.7076 | 71.0672 | 72.4495
Peak (CfD) revenue | Cr | 0 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695 | 118.3695
Total revenue | Cr | 0 | 163.3929 | 164.3173 | 165.2588 | 166.2177 | 167.1942 | 168.1886 | 169.2012 | 170.2322 | 171.2818 | 172.3504 | 173.4381 | 174.5452 | 175.672 | 176.8187 | 177.9856 | 179.1729 | 180.3809 | 181.6099 | 182.86 | 184.1315 | 185.4247 | 186.7398 | 188.0771 | 189.4367 | 190.819
O&M | Cr | 0 | 14.75 | 15.4875 | 16.2619 | 17.075 | 17.9287 | 18.8252 | 19.7664 | 20.7547 | 21.7925 | 22.8821 | 24.0262 | 25.2275 | 26.4889 | 27.8133 | 29.204 | 30.6642 | 32.1974 | 33.8073 | 35.4976 | 37.2725 | 39.1361 | 41.0929 | 43.1476 | 45.305 | 47.5702
EBITDA | Cr | 0 | 148.6429 | 148.8298 | 148.9969 | 149.1427 | 149.2655 | 149.3635 | 149.4348 | 149.4775 | 149.4893 | 149.4683 | 149.4119 | 149.3177 | 149.1831 | 149.0054 | 148.7816 | 148.5087 | 148.1835 | 147.8026 | 147.3623 | 146.859 | 146.2886 | 145.6469 | 144.9295 | 144.1317 | 143.2487
Depreciation | Cr | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
Taxable income | Cr | 0 | 110.6429 | 110.8298 | 110.9969 | 111.1427 | 111.2655 | 111.3635 | 111.4348 | 111.4775 | 111.4893 | 111.4683 | 111.4119 | 111.3177 | 111.1831 | 111.0054 | 110.7816 | 110.5087 | 110.1835 | 109.8026 | 109.3623 | 108.859 | 108.2886 | 107.6469 | 106.9295 | 106.1317 | 105.2487
Tax | Cr | 0 | 27.6607 | 27.7074 | 27.7492 | 27.7857 | 27.8164 | 27.8409 | 27.8587 | 27.8694 | 27.8723 | 27.8671 | 27.853 | 27.8294 | 27.7958 | 27.7513 | 27.6954 | 27.6272 | 27.5459 | 27.4506 | 27.3406 | 27.2147 | 27.0721 | 26.9117 | 26.7324 | 26.5329 | 26.3122
Capex | Cr | -950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unlevered FCF | Cr | -950 | 120.9822 | 121.1223 | 121.2477 | 121.357 | 121.4491 | 121.5226 | 121.5761 | 121.6081 | 121.617 | 121.6012 | 121.5589 | 121.4883 | 121.3873 | 121.254 | 121.0862 | 120.8815 | 120.6376 | 120.3519 | 120.0218 | 119.6442 | 119.2164 | 118.7352 | 118.1971 | 117.5988 | 116.9365

## 5.Financing_EIRR
FINANCING & EQUITY IRR (base case, market multiplier = 1.0)
Equity IRR | 17.36% |  | Debt = 70% x capex; 15-yr equal-principal @ 9%. Tax shield on interest included.
Rs Cr | Unit | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
EBITDA (from Cashflow) | Cr | 0 | 148.6429 | 148.8298 | 148.9969 | 149.1427 | 149.2655 | 149.3635 | 149.4348 | 149.4775 | 149.4893 | 149.4683 | 149.4119 | 149.3177 | 149.1831 | 149.0054 | 148.7816 | 148.5087 | 148.1835 | 147.8026 | 147.3623 | 146.859 | 146.2886 | 145.6469 | 144.9295 | 144.1317 | 143.2487
Debt balance (open) | Cr | 665 | 665 | 620.6667 | 576.3333 | 532 | 487.6667 | 443.3333 | 399 | 354.6667 | 310.3333 | 266 | 221.6667 | 177.3333 | 133 | 88.6667 | 44.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest | Cr | 0 | 59.85 | 55.86 | 51.87 | 47.88 | 43.89 | 39.9 | 35.91 | 31.92 | 27.93 | 23.94 | 19.95 | 15.96 | 11.97 | 7.98 | 3.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Principal repay | Cr | 0 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 44.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Depreciation | Cr | 0 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
Taxable income | Cr | 0 | 50.7929 | 54.9698 | 59.1269 | 63.2627 | 67.3755 | 71.4635 | 75.5248 | 79.5575 | 83.5593 | 87.5283 | 91.4619 | 95.3577 | 99.2131 | 103.0254 | 106.7916 | 110.5087 | 110.1835 | 109.8026 | 109.3623 | 108.859 | 108.2886 | 107.6469 | 106.9295 | 106.1317 | 105.2487
Tax | Cr | 0 | 12.6982 | 13.7424 | 14.7817 | 15.8157 | 16.8439 | 17.8659 | 18.8812 | 19.8894 | 20.8898 | 21.8821 | 22.8655 | 23.8394 | 24.8033 | 25.7563 | 26.6979 | 27.6272 | 27.5459 | 27.4506 | 27.3406 | 27.2147 | 27.0721 | 26.9117 | 26.7324 | 26.5329 | 26.3122
Equity cash flow | Cr | -285 | 31.7613 | 34.894 | 38.0118 | 41.1137 | 44.1983 | 47.2643 | 50.3103 | 53.3348 | 56.3362 | 59.3129 | 62.2631 | 65.1849 | 68.0765 | 70.9357 | 73.7604 | 120.8815 | 120.6376 | 120.3519 | 120.0218 | 119.6442 | 119.2164 | 118.7352 | 118.1971 | 117.5988 | 116.9365

## 6.Sensitivity
SENSITIVITY: MARKET PRICE +/-10% (same strike) -> Equity IRR & Pool economics
Strike held constant. A price move flexes (i) merchant day-sales and (ii) gain-share above strike; pool top-up = what SECI pays the developer.
SUMMARY
| Market -10% | Base | Market +10%
Market price multiplier | 0.9 | 1 | 1.1
Equity IRR | 16.32% | 17.36% | 18.39%
Change vs base (ppt) | -1.0331 | 0 | 1.0363
Realized peak price yr1 (Rs/kWh) | 10.81 | 10.81 | 10.81
SECI pool top-up yr1 (Rs Cr, + = SECI pays) | 59.2395 | 52.6695 | 46.0995
EQUITY CASH FLOW ENGINE (Rs Cr) - drives the IRRs above
Year | Market -10% | Base | Market +10%
0 | -285 | -285 | -285
1 | 28.3846 | 31.7613 | 35.1381
2 | 31.4479 | 34.894 | 38.3401
3 | 34.4951 | 38.0118 | 41.5285
4 | 37.5251 | 41.1137 | 44.7023
5 | 40.5364 | 44.1983 | 47.8601
6 | 43.5278 | 47.2643 | 51.0007
7 | 46.4979 | 50.3103 | 54.1226
8 | 49.4451 | 53.3348 | 57.2245
9 | 52.3678 | 56.3362 | 60.3046
10 | 55.2643 | 59.3129 | 63.3614
11 | 58.1329 | 62.2631 | 66.3932
12 | 60.9717 | 65.1849 | 69.3981
13 | 63.7788 | 68.0765 | 72.3742
14 | 66.552 | 70.9357 | 75.3194
15 | 69.2892 | 73.7604 | 78.2316
16 | 116.3213 | 120.8815 | 125.4418
17 | 115.9868 | 120.6376 | 125.2885
18 | 115.6089 | 120.3519 | 125.095
19 | 115.185 | 120.0218 | 124.8585
20 | 114.7121 | 119.6442 | 124.5764
21 | 114.1873 | 119.2164 | 124.2456
22 | 113.6074 | 118.7352 | 123.8629
23 | 112.969 | 118.1971 | 123.4252
24 | 112.2688 | 117.5988 | 122.9288
25 | 111.5028 | 116.9365 | 122.3703
READING IT:
- Equity IRR is fairly insulated: the two-way CfD floors peak revenue at the strike, so only merchant sales + the 50% gain-share flex with price.
- A +10% market lifts EIRR ~1 ppt and CUTS SECI pool top-up (developer needs less support and shares upside back).
- A -10% market lowers EIRR ~1 ppt and RAISES SECI pool top-up (SECI covers a bigger gap to the strike).
- This asymmetric protection is the point of a CfD: the developer carries limited merchant risk, the procurer carries the pool-cost risk.